## Summary
Data Centre Electrical Design: 2N architecture (summary)
1 MW IT scenario. All values link to the calculation sheets. Change Inputs to re-size the design.
Item | Result | Unit | Where calculated
IT load | 1000 | kW | Inputs
Total facility load | 1500 | kW | Inputs
PUE | 1.5 | - | Inputs
Design load per path (failover + growth) | 2000 | kVA | Load_Calc
Transformer per path | 2500 | kVA | Sizing
Transformer loading, normal / failover | 33% / 67% |  | Sizing
UPS per path | 1200 | kVA | Sizing
UPS loading, normal / failover | 42% / 83% |  | Sizing
Battery per UPS (installed) | 4 strings x 300 Ah, 480 V, 10 min |  | Sizing
Generator per path | 2500 | kVA | Sizing
Fuel tank per generator | 9720 | L | Sizing
PDUs per path | 4 x 400 kVA |  | Sizing
Fault level at LV bus (incl. motors) | 51.246 | kA | ShortCircuit
LV equipment breaking rating | 65 | kA | ShortCircuit
Voltage drop, UPS output to rack | 2.369% |  | Cables
Availability, single path | 99.92% |  | Reliability
Availability, 2N | 100% |  | Reliability
Expected downtime, 2N | 4.3563 | min/year | Reliability
Expected downtime, single path | 6.7417 | h/year | Reliability
Design checks
Check | Status
Transformer loading (failover + growth) within limit | OK
UPS can carry 100% IT load after other path fails | OK
PDU can carry 100% IT load after other path fails | OK
Generator covers failover facility load | OK
Cable ampacity (all feeders) | OK
Cable voltage drop (all feeders and total) | OK
Cable short-circuit withstand | OK
Breaking capacity >= fault level (all points) | OK
Breaker frame and Ir coordination with load | OK
MV relay graded above LV main ACB | OK
Rack branch current within 80% of breaker | OK
Overall | ALL CHECKS PASS
Sheets: Inputs > Load_Calc > Sizing > Cables > ShortCircuit > Protection > Reliability > Failure_Scenarios > BOM > Std_Sizes
Colour legend: blue on yellow = input; black = formula; green = link from another sheet. Hardcoded assumptions are documented next to the cell.

## Inputs
Inputs and design basis
Blue text on yellow = editable input. Black = formula. All other sheets recalculate from here.
Parameter | Value | Unit | Source / remark
1. Facility load definition
Number of racks | 200 | nos | Project scenario (assumption)
Average IT load per rack | 5 | kW | Typical enterprise / colocation density
Total IT load | 1000 | kW | Calculated
Cooling load (chillers, CRAH, pumps) | 400 | kW | Assumption: ~80% of overhead so that PUE ≈ 1.5
Lighting, security, BMS, fire and other auxiliaries | 60 | kW | Assumption
UPS and distribution losses | 40 | kW | Assumption: ~4% of IT load
Total facility load | 1500 | kW | Calculated
PUE (derived) | 1.5 | - | Target about 1.5
2. Electrical design basis
Facility power factor at LV (before correction) | 0.9 | - | Assumption (mixed IT + mechanical load)
Future growth margin | 20% | - | Design margin on load (20-30% typical)
Maximum transformer loading at design (failover + growth) | 85% | - | Design rule: keep thermal margin
Utility MV supply voltage | 11 | kV | Typical DISCOM supply; confirm with PSPCL
LV system voltage | 415 | V | 3-phase 4-wire, 50 Hz, TN-S
Utility fault level at 11 kV | 250 | MVA | ASSUMPTION (about 13 kA). Obtain the real value from the DISCOM
Transformer impedance | 0.0625 | pu | 6.25% typical for 2500 kVA (IS 2026)
Design ambient temperature | 45 | °C | Punjab summer design condition
Temperature derating factor, XLPE at 45°C | 0.87 | - | IEC 60364-5-52 (reference 30°C)
Grouping derating factor | 0.8 | - | Multiple circuits on a tray (assumption)
3. UPS and battery
UPS output power factor (kW/kVA) | 1 | - | Modern double-conversion UPS (IEC 62040-3)
UPS efficiency (double conversion) | 0.96 | - | Typical 95-97%
Battery recharge allowance on UPS input | 1.1 | - | 10% extra input while recharging
UPS input power factor | 0.99 | - | Active / IGBT front end
Battery autonomy | 10 | min | Typical 5-15 min until generator is stable
Number of VRLA cells per string | 240 | nos | 240 cells x 2 V = 480 V nominal DC bus
End-of-discharge voltage per cell | 1.67 | V | Typical for high-rate discharge
Battery ageing factor | 1.25 | - | End of life at 80% capacity
Battery design margin | 1.1 | -
Usable fraction of nominal energy at 10 min rate | 0.55 | - | PRELIMINARY. Validate with manufacturer constant-power tables
Battery string capacity (nominal) | 300 | Ah | Selected block size (assumption)
4. Generator
Generator power factor | 0.8 | - | Standard genset rating
Derating for UPS rectifier harmonics and step load | 1.1 | - | 1.10 for active front end; 1.25-1.4 for 6-pulse rectifier
Generator sub-transient reactance X''d | 0.12 | pu | Typical 10-15%
Extra standby gensets per path (N+1) | 0 | nos | 0 = one genset per path. Set 1 for N+1 per path
Fuel autonomy | 24 | h | Design choice (Tier III needs minimum 12 h)
Specific fuel consumption | 0.27 | L/kWh | Typical diesel genset at 75% load
5. PDU, RPP and rack
PDUs per path | 4 | nos | Design choice
IT load power factor | 0.95 | -
Maximum PDU loading | 80% | - | Design rule
RPPs per PDU | 2 | nos | Design choice
Rack branch voltage (1-phase) | 230 | V
Rack branch breaker | 32 | A | 32 A MCB per rack feed
6. Motor load (short-circuit contribution)
Motor load connected to LV board | 400 | kW | Assumes all cooling load as motors (conservative)
Motor power factor | 0.85 | -
Motor contribution multiple of FLC | 5 | x | IEC 60909: 4-6 x FLC
7. Feeder route lengths
LV essential board to UPS input | 40 | m | Layout assumption
UPS output board to PDU | 30 | m | Layout assumption
LV essential board to mechanical MCC | 60 | m | Layout assumption
RPP to rack | 25 | m | Layout assumption
8. Architecture
Redundancy | 2N | - | Two fully independent paths, A and B

## Load_Calc
Step 1: Load calculation
Each path (A or B) must carry the complete facility load when the other path is lost (2N).
Parameter | Value | Unit | Source / remark
Facility load
IT load | 1000 | kW
Cooling | 400 | kW
Auxiliaries | 60 | kW
UPS and distribution losses | 40 | kW
Total facility load | 1500 | kW
Total facility apparent power | 1666.6667 | kVA | kW / power factor
Per-path loading
Each path, normal operation (50% share) | 750 | kW | A and B share load equally
Each path, normal operation | 833.3333 | kVA
Each path, failover (100% of load) | 1500 | kW | One path carries everything after the other fails
Each path, failover | 1666.6667 | kVA
Design values with growth margin
Design load per path (failover + growth) | 1800 | kW
Design apparent power per path | 2000 | kVA | Used for transformer sizing
Design IT load per path (failover + growth) | 1200 | kW | Used for UPS and PDU sizing
Load breakdown | kW | % of total
IT load | 1000 | 66.67%
Cooling | 400 | 26.67%
Auxiliaries | 60 | 4%
Losses | 40 | 2.667%

## Sizing
Step 3: Equipment sizing (per path)
Quantities in the BOM are per path x 2. Results update from Inputs.
Parameter | Value | Unit | Source / remark
Transformer
Required kVA = design kVA / max loading | 2352.9412 | kVA
Selected transformer | 2500 | kVA | Next standard size. 11/0.415 kV, Dyn11, ONAN, Z = 6.25%
LV full-load current | 3478.0137 | A
MV full-load current | 131.216 | A
Loading, normal (50% share) | 33.33%
Loading, failover (100%) | 66.67% |  | Without growth margin
Loading, failover + growth | 80% |  | Must be <= max loading
TR secondary busduct / ACB frame | 4000 | A | Smallest standard frame >= full-load current
UPS
Required UPS = design IT load / UPS PF | 1200 | kVA
Selected UPS (per path) | 1200 | kVA | Next standard size
UPS loading, normal (50% IT) | 41.67% |  | Note: UPS efficiency falls at low load
UPS loading, failover (100% IT) | 83.33% |  | Must be <= 100%
UPS output current at rated load | 1669.4466 | A
UPS input apparent power (incl. battery recharge) | 1388.8889 | kVA
UPS input current | 1932.2298 | A
Battery (preliminary, validate against manufacturer discharge tables)
DC power at rated UPS load | 1250 | kW
Energy for autonomy | 208.3333 | kWh
Nominal energy needed (ageing, margin, usable fraction) | 520.8333 | kWh
Nominal DC bus voltage | 480 | V
Required capacity at nominal voltage | 1085.0694 | Ah
Number of strings | 4 | nos
Installed capacity | 1200 | Ah
Installed nominal energy | 576 | kWh
Discharge current at end-of-discharge voltage | 3118.7625 | A
Discharge current per string | 779.6906 | A
Generator
Required kW = design load x harmonic/step derating | 1980 | kW
Required kVA | 2475 | kVA
Selected genset | 2500 | kVA | Next standard size
Genset kW rating | 2000 | kW
Genset loading at present failover load | 75%
Genset loading when both gensets share load | 37.5% |  | Below ~30% risks wet stacking. Plan load-bank tests
Gensets per path (N + extra) | 1 | nos
Genset full-load current | 3478.0137 | A
Fuel consumption at failover load | 405 | L/h
Fuel tank per genset | 9720 | L
PDU, RPP and rack
Required PDU kVA | 394.7368 | kVA
Selected PDU | 400 | kVA
PDU loading, failover | 65.79%
PDU rated current | 556.4822 | A
Racks per PDU | 50 | nos
RPPs per path | 8 | nos
Rack feed current at failover (single side carries 100%) | 22.8833 | A | 1-phase
Branch check: current <= 80% of breaker | OK

## Cables
Step 3b: Cable sizing and voltage drop
Cu XLPE cable. Number of parallel runs is calculated so that derated ampacity >= load current. Voltage-drop limit 3% per feeder.
Feeder | Load current Ib (A) | Voltage (V) | Phases | Length (m) | cos φ | Cable size (mm²) | Ampacity per run (A) | Derating | Parallel runs | Installed capacity (A) | Ampacity check | R (Ω/km) | X (Ω/km) | Voltage drop (V) | Voltage drop (%) | Limit (%) | VD check | Fault at source (kA) | Clearing time (s) | Min size per run, adiabatic (mm²) | Withstand check
LV essential board to UPS input | 1932.2298 | 415 | 3 | 40 | 0.99 | 300 | 631 | 0.696 | 5 | 2195.88 | OK | 0.077 | 0.071 | 2.3091 | 0.5564% | 3% | OK | 51.246 | 0.3 | 39.2568 | OK
UPS output board to PDU | 556.4822 | 415 | 3 | 30 | 0.95 | 185 | 460 | 0.696 | 2 | 640.32 | OK | 0.126 | 0.073 | 2.0602 | 0.4964% | 3% | OK | 41.0807 | 0.2 | 64.2373 | OK
LV essential board to mechanical MCC | 752.8877 | 415 | 3 | 60 | 0.85 | 240 | 546 | 0.696 | 2 | 760.032 | OK | 0.096 | 0.072 | 4.6761 | 1.127% | 3% | OK | 51.246 | 0.3 | 98.142 | OK
RPP to rack branch (1-phase) | 22.8833 | 230 | 1 | 25 | 0.95 | 6 | 54 | 0.696 | 1 | 37.584 | OK | 3.93 | 0.1 | 4.3075 | 1.873% | 3% | OK | 29.8876 | MCB let-through | 1.64 | OK
Total voltage drop, UPS output to rack (feeder 2 + feeder 4) | [14 empty] | 2.369% | 5% | OK
Notes:
1. Derating = temperature factor x grouping factor (Inputs). Ampacity table is indicative; verify with vendor data.
2. Voltage drop: 3-phase = √3·I·L·(R·cosφ + X·sinφ); 1-phase = 2·I·L·(R·cosφ + X·sinφ). Per-run current used.
3. Adiabatic check: S >= I·√t / k with k = 143 (Cu, XLPE 90°C to 250°C, IEC 60364-4-43), assuming equal current sharing between parallel runs.
4. Busduct (not cable) is proposed for transformer-to-LV board and generator-to-ATS links, rated per Sizing sheet.
Rack MCB let-through energy I²t (A²s) | 55000 | ASSUMPTION: typical class-3 32 A MCB (EN 60898). Verify with the breaker datasheet.

## ShortCircuit
Step 4a: Short-circuit calculation
Balanced 3-phase fault, impedance method. Impedances summed arithmetically (conservative). Verify with ETAP/pandapower for final design.
Parameter | Value | Unit | Source / remark
Source and transformer
Base impedance at LV (V² / S) | 68.89 | mΩ
Utility source impedance on transformer base | 0.01 | pu
Total source + transformer impedance | 0.0725 | pu
Total impedance at LV bus | 4.9945 | mΩ
Fault current from utility at LV bus | 47.9726 | kA
Motor full-load current | 654.6849 | A
Motor contribution | 3.2734 | kA
Fault levels and equipment rating
Fault point | Impedance to point (mΩ) | Fault current (kA) | Note | Selected breaking rating (kA) | Check
F1 MV bus (11 kV) |  | 13.1216 | MV switchgear rating | 16 | OK
F2 LV essential bus (incl. motors) | 4.9945 | 51.246 | LV ACB / switchboard rating | 65 | OK
F3 UPS output board (on static bypass) | 5.8324 | 41.0807 | UPS output board must withstand bypass fault | 50 | OK
F4 PDU incomer | 8.0167 | 29.8876 | PDU incomer breaker | 36 | OK
F5 Rack branch (phase-neutral) | 204.5803 | 1.1243 | Rack MCB (line-neutral loop, 2 x branch cable) | 6 | OK
F6 Generator terminals |  | 28.9834 | Generator contribution only; gensets are not paralleled with the utility | 65 | OK

## Protection
Step 4b: Protection devices and coordination
Settings are proposed starting values for the coordination study. Blue = editable setting.
Device / location | Load current (A) | Frame (A) | Ir setting (A) | Isd multiple (x Ir) | Isd pickup (A) | tsd delay (s) | Fault at device (kA) | Breaking rating (kA) | Frame >= Ir >= Ib | Isd < fault current (sensitivity) | Rating >= fault
LV main ACB (TR secondary) | 3478.0137 | 4000 | 3700 | 5 | 18500 | 0.4 | 51.246 | 65 | OK | OK | OK
UPS input ACB | 1932.2298 | 2500 | 2050 | 6 | 12300 | 0.3 | 51.246 | 65 | OK | OK | OK
UPS output ACB | 1669.4466 | 2500 | 1800 | 6 | 10800 | 0.2 | 41.0807 | 50 | OK | OK | OK
PDU main MCCB | 556.4822 | 800 | 600 | 8 | 4800 | 0.1 | 29.8876 | 36 | OK | OK | OK
Mechanical MCC feeder ACB | 752.8877 | 1000 | 800 | 6 | 4800 | 0.3 | 51.246 | 65 | OK | OK | OK
Rack branch MCB (C-curve) | 22.8833 | 32 | 32 | 10 | 320 | 0 | 1.1243 | 6 | OK | OK | OK
MV transformer protection (11 kV relay, IEC Normal Inverse)
Parameter | Value | Unit | Remark
Transformer MV full-load current | 131.216 | A
Relay time multiplier (TMS) | 0.25 | - | Chosen to grade above LV main ACB
51 pickup = 1.25 x FLC (rounded up to 10 A) | 170 | A | Primary side
Max LV bus fault reflected to 11 kV | 1933.3728 | A
Fault multiple of pickup | 11.3728 | x
Relay operating time at that fault | 0.70244 | s | IEC NI: t = TMS x 0.14 / ((I/Is)^0.02 - 1)
Grading margin over LV main ACB tsd | 0.30244 | s | Need >= 0.3 s
Grading check | OK
50 pickup = 1.15 x reflected LV fault (rounded up to 100 A) | 2300 | A | Must not trip for LV-side faults
Transformer inrush (10 x FLC) | 1312.1597 | A
50 pickup above inrush and below MV bus fault | OK
Selectivity chain (fault on downstream side, trip delays)
Upstream device | Delay (s) | Downstream device | Delay (s) | Margin (s) | Check (>= 0.1 s)
UPS output ACB | 0.2 | PDU main MCCB | 0.1 | 0.1 | OK
UPS input ACB | 0.3 | UPS output ACB | 0.2 | 0.1 | OK
LV main ACB | 0.4 | UPS input ACB | 0.3 | 0.1 | OK
LV main ACB | 0.4 | Mechanical MCC feeder | 0.3 | 0.1 | OK
11 kV relay (51) | 0.70244 | LV main ACB | 0.4 | 0.30244 | OK
Other protection and safety provisions:
Transformer: Buchholz relay, winding and oil temperature (WTI/OTI), pressure relief valve; restricted earth fault (REF) on LV neutral.
Generator: 27/59 voltage, 81 frequency, 50/51 overcurrent, 32 reverse power, 87G differential, 64 earth fault, emergency stop.
Earthing: TN-S at LV, solidly earthed transformer neutral, earth pit resistance target < 1 Ω (IS 3043), separate IT/clean earth bonded at one point.
Surge protection: Type 1 at LV main board, Type 2 at UPS input and PDU, Type 3 at critical rack strips (IEC 61643).
Arc flash: not computed here. Recommended as an extension (IEEE 1584) once the final breaker data is available.

## Reliability
Step 5: Reliability and availability analysis
Series reliability block model per path; 2N combines two independent paths with a common-cause factor. Component data are ILLUSTRATIVE ASSUMPTIONS: replace with IEEE 493 / vendor data.
Parameter | Value | Unit | Remark
Utility supply availability (per feeder) | 99.5% | - | ASSUMPTION. Replace with DISCOM reliability data (SAIDI/SAIFI) for the feeder
Generator start-on-demand availability | 99% | - | ASSUMPTION. Depends on maintenance and testing regime
Common-cause factor between paths (beta) | 1% | - | ASSUMPTION. Fraction of path failures that hit both paths (shared room, fire, human error)
Power source availability (utility with generator backup) | 100% | - | Formula: 1 - (1 - A_utility) x (1 - A_generator)
Component (series, per path) | MTBF (h) | MTTR (h) | Unavailability | Availability
MV switchgear | 500000 | 24 | 4.7998e-05 | 100%
Transformer | 300000 | 130 | 0.00043315 | 99.96%
LV essential switchboard | 1000000 | 24 | 2.3999e-05 | 100%
ATS | 250000 | 8 | 3.1999e-05 | 100%
UPS module incl. static switch | 120000 | 8 | 6.6662e-05 | 99.99%
Battery system | 100000 | 8 | 7.9994e-05 | 99.99%
UPS output board | 1000000 | 24 | 2.3999e-05 | 100%
PDU | 500000 | 4 | 7.9999e-06 | 100%
RPP | 1000000 | 4 | 4e-06 | 100%
Configuration | Availability | Unavailability | Downtime (h/year) | Downtime (min/year) | Availability class (Uptime Institute figures)
N: single path, no redundancy | 99.92% | 0.0007696 | 6.7417 | 404.5035 | Tier II level (>= 99.741%)
N+1: parallel redundant UPS, rest single path | 99.94% | 0.00062453 | 5.4709 | 328.2537 | Tier II level (>= 99.741%)
2N: two independent paths (this design) | 100% | 8.2883e-06 | 0.072606 | 4.3563 | Tier IV level (>= 99.995%)
Notes:
1. Availability class is a calculated comparison only. Formal Tier certification depends on topology and operations, not on this figure.
2. The transformer dominates single-path unavailability because of its long repair time; this is why 2N (or a spare transformer) matters.
3. 2N unavailability = U_path² + β·U_path. Without the β term, 2N would appear unrealistically perfect.
4. Rack-level dual-corded PSU failure and operator error are not modelled.

## Failure_Scenarios
Step 5b: Failure scenario table (FMEA style)
What happens when a component fails. The last column is calculated live from the sizing sheets.
ID | Failure event | System response | Effect on IT load | Remaining risk / mitigation | Live check
F1 | Utility outage on both feeders | ATS senses loss, both gensets start and transfer in about 10-15 s; UPS batteries carry the load meanwhile. | None | Generators become the single source of energy. Fuel autonomy and monthly on-load tests are critical. | Gen load each = 38% of kW rating; battery = 10 min; fuel = 24 h
F2 | Utility feeder A lost (B healthy) | Path A ATS starts Gen A; UPS A rides through on battery. | None | Path B untouched. If Gen A fails to start, see F5. | UPS-A battery autonomy = 10 min
F3 | Transformer A internal fault | MV relay / Buchholz trips VCB. Path A LV board loses utility; ATS may start Gen A. | None (dual-corded loads stay on B) | Longest repair time in the system. Path B now runs at 100% of facility load; no redundancy until repair. | TR-B loading at failover = 67% of 2500 kVA
F4 | UPS A module failure | UPS transfers to static bypass if available, otherwise path A output is lost. Dual-corded racks continue from B. | None | UPS B now carries all IT load. | UPS-B loading at failover = 83% (limit 100%)
F5 | Generator A fails to start during utility outage | UPS A runs on battery until autonomy ends, then path A de-energises. | None while path B is healthy | If Gen B also fails, IT stops after battery autonomy. Mitigation: N+1 gensets, monthly testing, fuel quality management. | Battery ride-through = 10 min
F6 | PDU A failure | Downstream racks lose A feed; B feed takes the full rack load. | None | Rack feeds on B carry 100% of rack load. | Rack feed current on B = 22.9 A vs 32 A breaker (80% rule)
F7 | Planned maintenance of entire path A (concurrent maintainability) | Path A isolated at LV main and UPS output; B carries everything. | None | Facility is single-path during the work. Schedule in low-risk windows. | Path B loading: TR 67%, UPS 83%, PDU 66%
F8 | Short circuit at a PDU | PDU main MCCB clears in its instantaneous / short-time zone; upstream devices stay closed by time grading. | None | Needs the coordination study to confirm selectivity. | Fault at PDU = 29.9 kA; PDU main tsd = 0.1 s, UPS output tsd = 0.2 s
F9 | Common-cause event (fire / flood in a shared electrical room) | Both paths lost if A and B equipment share a room or cable route. | Total outage | Physical separation: separate fire-rated rooms and cable routes for A and B. This is the main 2N weakness. | Common-cause factor assumed = 1.0%
F10 | Single-corded load while STS fails | Single-corded equipment fed through STS loses supply if the STS itself fails or if both sources fail. | Only single-corded loads | Minimise single-corded equipment; use dual-corded or rack-level ATS. | Static transfer time is typically 4-8 ms (vendor data)

## BOM
Step 7: Equipment list / bill of quantities (no prices)
Quantity = per-path quantity x multiplier. Multiplier 2 for A/B items, 1 for shared items.
# | Item | Rating / description | Qty per path | Multiplier | Total qty | Remarks
1 | MV switchgear panel | 11 kV VCB panel, 630 A, 16 kA / 3 s | 2 | 2 | 4 | Incomer + transformer feeder per path
2 | Distribution transformer | 2500 kVA, 11/0.415 kV, Dyn11, Z = 6.25%, ONAN | 1 | 2 | 2 | Cast resin or oil, per local practice
3 | Busduct, transformer to LV board | 4000 A busduct | 1 | 2 | 2
4 | LV main ACB | 4000 A frame, Ir = 3700 A, 65 kA | 1 | 2 | 2
5 | Automatic transfer switch (ATS) | 4000 A, 4-pole, utility / generator | 1 | 2 | 2
6 | Diesel generator set | 2500 kVA standby, 415 V, 2000 kW | 1 | 2 | 2 | Set Inputs extra gensets = 1 for N+1 per path
7 | Fuel storage tank | 9,720 L (for 24 h at failover load) | 1 | 2 | 2 | Local fire and explosives rules apply
8 | LV essential switchboard | Form 4b, incl. UPS and mechanical feeders | 1 | 2 | 2
9 | UPS | 1200 kVA / kW, double conversion, IEC 62040 | 1 | 2 | 2
10 | Battery string | 300 Ah, 240 cells (480 V), VRLA | 4 | 2 | 8 | Strings per UPS; validate with vendor tables
11 | UPS output board | With maintenance bypass | 1 | 2 | 2
12 | PDU | 400 kVA, 415/230 V, with isolation transformer or static | 4 | 2 | 8
13 | RPP (remote power panel) | 42-way, 32 A outgoing MCBs, metered | 8 | 2 | 16
14 | Cable sets, LV board to UPS input | 5 x 3 x 1C 300 mm² Cu XLPE + PE | 5 | 2 | 10 | Qty = parallel runs
15 | Cable sets, UPS output board to PDU | 2 x 3 x 1C 185 mm² Cu XLPE + PE | 8 | 2 | 16 | Qty = runs x PDUs
16 | Cable sets, LV board to mechanical MCC | 2 x 3 x 1C 240 mm² Cu XLPE + PE | 2 | 2 | 4
17 | Rack branch cables | 1-phase, 6 mm² Cu XLPE, one per rack feed | 200 | 2 | 400 | A feed and B feed for every rack
18 | Rack PDU strips | Metered, 32 A, one per feed | 200 | 2 | 400
19 | IT racks | Dual-corded racks | 200 | 1 | 200 | Shared between paths
20 | Static transfer switch (STS) | 100 A class, for single-corded loads | 2 | 1 | 2 | PLACEHOLDER quantity. Depends on single-corded device count
21 | Surge protective devices | Type 1 at LV main, Type 2 at UPS input and PDU | 3 | 2 | 6 | Sets

## Std_Sizes
Standard ratings and cable data
Transformer (kVA) | UPS (kVA) | Genset (kVA) | PDU (kVA) | LV breaking (kA) | MV breaking (kA) | Breaker / busduct frame (A) | Branch MCB breaking (kA) | Cu XLPE size (mm²) | Ampacity in air @30°C (A) | R at 90°C (Ω/km) | X (Ω/km)
1000 | 500 | 1250 | 100 | 36 | 12.5 | 630 | 6 | 6 | 54 | 3.93 | 0.1
1250 | 600 | 1500 | 150 | 50 | 16 | 800 | 10 | 10 | 75 | 2.33 | 0.094
1600 | 800 | 1750 | 200 | 65 | 20 | 1000 | 15 | 16 | 100 | 1.47 | 0.09
2000 | 1000 | 2000 | 250 | 80 | 25 | 1250 | 25 | 25 | 133 | 0.927 | 0.086
2500 | 1200 | 2250 | 300 | 100 | 31.5 | 1600 |  | 35 | 164 | 0.668 | 0.083
3150 | 1250 | 2500 | 400 |  | 40 | 2000 |  | 50 | 198 | 0.494 | 0.081
4000 | 1500 | 2750 | 500 |  |  | 2500 |  | 70 | 253 | 0.342 | 0.078
| 1600 | 3000 |  |  |  | 3200 |  | 95 | 306 | 0.246 | 0.076
| 2000 |  |  |  |  | 4000 |  | 120 | 354 | 0.195 | 0.075
[6 empty] | 5000 |  | 150 | 402 | 0.159 | 0.074
[6 empty] | 6300 |  | 185 | 460 | 0.126 | 0.073
[8 empty] | 240 | 546 | 0.096 | 0.072
[8 empty] | 300 | 631 | 0.077 | 0.071
Note: cable values are indicative (1.1 kV Cu XLPE, single-core trefoil in air). Verify with the manufacturer's datasheet and installation method before procurement.